## Page_01
Note: When doing rounds be aware for unusual smells, sounds, sights, or anything not normal.
Engineer Initials:
Time of Round: | 02:00 | 08:00 | 14:00 | 20:00
DCF Office
Logs
Check Daily logs on Microsoft SharePoint | ✓ X | ✓ X | ✓ X | ✓ X
Check office white board for plant information | ✓ X | ✓ X | ✓ X | ✓ X
BMS
OAT (Over-the-Air Temperature)
Wet Bulb
Any BMS alarms? Note in comments below. | Yes / No | Yes / No | Yes / No | Yes / No
Chill Water Unit No. 1
Chill Water Unit No. 2
Chill Water Unit No. 3
Cooling Load_Mechanical Screen
Tower Load_Mechanical Screen
Total Power Usage_Electrical Screen
DCF Power Usage_Electrical Screen
PUE_Electrical Screen
Electrical Room_1st Floor
Fire Panel (Check for alarms on fire panel display)
Fire Alarm | ✓ X | ✓ X | ✓ X | ✓ X
Pre-alarm | ✓ X | ✓ X | ✓ X | ✓ X
Security | ✓ X | ✓ X | ✓ X | ✓ X
Supervisory | ✓ X | ✓ X | ✓ X | ✓ X
System Trouble | ✓ X | ✓ X | ✓ X | ✓ X
Other Event | ✓ X | ✓ X | ✓ X | ✓ X
Electrical Room_Lower Level
Room Temperature | ✓ X | ✓ X | ✓ X | ✓ X
EF 1
EF 2
Command Center
Fire Panel (Check for alarms on fire panel display)
Fire alarm | ✓ X | ✓ X | ✓ X | ✓ X
Pre-alarm | ✓ X | ✓ X | ✓ X | ✓ X
Security | ✓ X | ✓ X | ✓ X | ✓ X
Supervisory | ✓ X | ✓ X | ✓ X | ✓ X
System Trouble | ✓ X | ✓ X | ✓ X | ✓ X
Other Event | ✓ X | ✓ X | ✓ X | ✓ X
Vesda's
Server Room 1 | ✓ X | ✓ X | ✓ X | ✓ X
Server Room 2 | ✓ X | ✓ X | ✓ X | ✓ X
Server Room 3 | ✓ X | ✓ X | ✓ X | ✓ X
Leak Detection
Server Rooms | ✓ X | ✓ X | ✓ X | ✓ X
PDU 13 | ✓ X | ✓ X | ✓ X | ✓ X
Notes:

## Page_02
Server Room 2
CRAC 29 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 21 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 32 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
Humidifier |  | %RH |  | %RH |  | %RH |  | %RH
PDU 21 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 20 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 06 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 14 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
FM 200 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CRAC 27 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 28 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
SR2 CHW Loop
CRAC 17 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 16 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 19 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 18 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
PDU 17 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 16 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CRAC 34 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
FM 200 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CRAC 15 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 25 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 20 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
PDU 19 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 18 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 07 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 15 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
Tear off Sticky Mat | Yes / No |  | Yes / No |  | Yes / No |  | Yes / No
MDF
Tear off Sticky Mat | Yes / No |  | Yes / No |  | Yes / No |  | Yes / No
PDU 12 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CRAC 08 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
Humidifier | ✓ X | %RH | ✓ X | %RH | ✓ X | %RH | ✓ X | %RH
FM 200 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 05 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CRAC 09 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
East Battery Room
Rail 2 Batteries
CU2 Battery Circuit Breaker | Open / Closed
Eagle Eye Computer Alarms |  | Voltage
Resistance
Temerature
DC Ground Fault Module reading below 6MA Pre-alarm=10MA, Alarm=20MA | ✓ X | ✓ X | ✓ X |  | ✓ X |  | ✓ X
Spare Battery Charger |  | Volts
Amps
Notes:

## Page_03
Rail 3 Batteries
Room Temperature | ✓ X | ✓ X | ✓ X | ✓ X
CU3 Battery Breaker
Eagle Eye Computer Alarms
DC Ground Fault Module reading below 6ma (Set Points are 10ma-Prealarm /20ma-Alarm) | ✓ X | ✓ X | ✓ X | ✓ X
East UPS Room
Battery Room Hydrogen Monitor Levels %
Rail 2
BOLD-RED-Ensure key is in locked position before touching STS display screen
STS-2A on preferred Source #1 | ✓ X | ✓ X | ✓ X | ✓ X
STS-2B on preferred Source #1 | ✓ X | ✓ X | ✓ X | ✓ X
STS-2C on preferred Source #1 | ✓ X | ✓ X | ✓ X | ✓ X
STS-2D on preferred Source #1 | ✓ X | ✓ X | ✓ X | ✓ X
CRAC 37
CRAC 36
CU2-M1_UPS 2
MBB Module Battery Breaker | ✓ X | ✓ X | ✓ X | ✓ X
CI2
CI2-B08 Breaker SPD_3 Green lights (Protected) | Yes / No | Yes / No | Yes / No | Yes / No
CI2-B11 CU2-M1 Input Breaker | ✓ X | ✓ X | ✓ X | ✓ X
CI2-B06 Static Bypass Breaker | ✓ X | ✓ X | ✓ X | ✓ X
Eaton Xpert meter Events light OFF (User is X and PW is X) | Yes / No | Yes / No | Yes / No | Yes / No
CI2-B05 Maintenance Bypass Breaker | ✓ X | ✓ X | ✓ X | ✓ X
CO2
Eaton Breaker Interface Module II Alarm light OFF
CO2-B18 Spare is Open
CO2-B11 STS-2A is Closed
CO2-B12 STS-2B is Closed
CO2-B17 Spare is Open
CO2-B13 STS-1A Closed
CO2-B14 STS-3B is Closed
CO2-B15 STS-2C is Closed
CO2-B16 STS-2D is Closed
Eaton Xpert meter Events light OFF (User is X and PW is X)
CO2-B01 CC-CO Isolation switch is Closed
Notes:

## Page_04
CC3
CC3-B05 (MBB) Breaker is Open
CC3-B01 (MIB) Breaker is Closed
CC3-B99 (LBB) Breaker is Open
Ensure Key is in Locked position before touching STS screen
STS3A is on preferred source 1
STS3B is on preferred source 1
EF 4
EF 5
East Electrical Room Leak Detection
Tear off sticky mat for SR3 (East side)
Fire Pump/ Pre action Room
Only on the 20:00 rounds check pre action valves to make sure they’re open (if open put a check next to each zone): | Zone 1 | Zone 5
| Zone 2 | Zone 6
| Zone 3 | Zone 7
Zone 4
Wet system level 1-4
Wet system level 0 (Corridors)
Jockey pump controller in Auto
Fire pump controller in Auto
Fire pump is on Normal source power
System water pressure left side of controller (140 -150psi)
System Nitorgen PSI (inside the red cabinet)
At Nitrogen tank regulator: (Replace with Extra Dry Nitrogen at 200PSI)
Main building water meter (Total) readings (Top reading)
Is Building Main-Drain Water Leaking?
If drain pipe has water leaking, check the air-bleed-off-valve in the penthouse stairwell for leaks.
Loading Dock Area
Do we need to order salt? If yes let the Chief Engineer know.
Check brine level (should be at the indicating line).
HP LL- 5 Ok (Fan is ok, If there's sweating of pipes check operation of HP)
Mechanical / Chill Water Units Room
Cooling Twr. Supply water meter reading.
Write down the water softener gallon readings from each softener.
Well meter reading
HP LL- 4 Ok (Fan is ok, If there's sweating of pipes check operation of HP)
CHWP #3
CHWP #5
CHWP #2
CHWP #4
CHWP #1
CDW to CHW makeup
CHW
CHW Filter PSI (23psi)
Bladder tank pressure (<30)
CHW Lakos Bag filter
Condenser Supply Temp. East Side (68 – 85)
CWP-6 VFD
CWP-1 VFD
CWP-4 VFD
CWP-3 VFD
CDWF VFD
CWP-2 VFD
CWP-5 VFD
TWR Fan- 6 VFD
TWR Fan- 5 VFD
CHWR Header Temp East
CHWR Temp (Bypass) East
Lakos Separator (6psi)
CHWS Temp East
CHWP #3 VFD
Well VFD
CHWP #2 VFD
CHWP #4 VFD
CHWP #1 VFD
CHWP #5 VFD
EF #6 VFD
Core Pump #1 VFD
Core Pump #2 VFD
HP LL- 3 Ok (Fan is ok, If there's sweating of pipes check operation of HP)
Core Pump #2 (15 - 20 PSID)
Core Pump #1 (15 - 20 PSID)
Condenser Supply Temp. West Side (68 – 85)
Chemical tanks level (above the order lines)
Nalco controller
Coupon Rack flow is between 4 – 6 GPM
Tower #4 VFD
Tower #3 VFD
Tower #2 VFD
Tower #1 VFD
Notes:

## Page_11
Server Room 1
Tear off sticky mat (Battery Room) | Yes / No |  | Yes / No |  | Yes / No |  | Yes / No
CRAC 24 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 23 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
SR1 CHW Loop | D/P |  | D/P |  | D/P |  | D/P
CRAC 04 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
PDU 11 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 09 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 02 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 04 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CRAC 26 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 05 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 06 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
PDU 01 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 08 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CRAC 33 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 07 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
Humidifier | ✓ X | %RH | ✓ X | %RH | ✓ X | %RH | ✓ X | %RH
FM 200 (2 tanks) | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
Tear off sticky mat (Hallway) | Yes / No |  | Yes / No |  | Yes / No |  | Yes / No
Server Room 3
Tear of sticky mat (Hallway) | Yes / No |  | Yes / No |  | Yes / No |  | Yes / No
CRAC 10 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 22 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 31 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
PDU 23 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 22 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 03 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 10 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CRAC 11 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 12 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 13 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 14 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 30 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
Humidifier | ✓ X | %RH | ✓ X | %RH | ✓ X | %RH | ✓ X | %RH
FM 200 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
Tear off sticky mat (Loading Dock) | Yes / No |  | Yes / No |  | Yes / No |  | Yes / No
Final Notes: