## Page_01
Note: When doing rounds be aware for unusual smells, sounds, sights, or anything not normal.
Engineer Initials:
Time of Round: | 02:00 | 08:00 | 14:00 | 20:00
DCF Office
Logs
Check Daily logs on Microsoft SharePoint | ✓ X | ✓ X | ✓ X | ✓ X
Check office white board for plant information | ✓ X | ✓ X | ✓ X | ✓ X
BMS
OAT (Over-the-Air Temperature) | °F | °F | °F | °F
Wet Bulb | °F | °F | °F | °F
Any BMS alarms? Note in comments below. | Yes / No | Yes / No | Yes / No | Yes / No
Chill Water Unit No. 1 | kW | kW | kW | kW
Chill Water Unit No. 2 | kW | kW | kW | kW
Chill Water Unit No. 3 | kW | kW | kW | kW
Cooling Load_Mechanical Screen | tR | tR | tR | tR
Tower Load_Mechanical Screen | tR | tR | tR | tR
Total Power Usage_Electrical Screen | kW | kW | kW | kW
DCF Power Usage_Electrical Screen | kW | kW | kW | kW
PUE_Electrical Screen
Electrical Room_1st Floor
Fire Panel (Check for alarms on fire panel display)
Fire Alarm | ✓ X | ✓ X | ✓ X | ✓ X
Pre-alarm | ✓ X | ✓ X | ✓ X | ✓ X
Security | ✓ X | ✓ X | ✓ X | ✓ X
Supervisory | ✓ X | ✓ X | ✓ X | ✓ X
System Trouble | ✓ X | ✓ X | ✓ X | ✓ X
Other Event | ✓ X | ✓ X | ✓ X | ✓ X
Electrical Room_Lower Level
Room Temperature | ✓ X | ✓ X | ✓ X | ✓ X
EF 1 | Hz | Hz | Hz | Hz
EF 2 | Hz | Hz | Hz | Hz
Command Center
Fire Panel (Check for alarms on fire panel display)
Fire alarm | ✓ X | ✓ X | ✓ X | ✓ X
Pre-alarm | ✓ X | ✓ X | ✓ X | ✓ X
Security | ✓ X | ✓ X | ✓ X | ✓ X
Supervisory | ✓ X | ✓ X | ✓ X | ✓ X
System Trouble | ✓ X | ✓ X | ✓ X | ✓ X
Other Event | ✓ X | ✓ X | ✓ X | ✓ X
Vesda's
Server Room 1 | ✓ X | ✓ X | ✓ X | ✓ X
Server Room 2 | ✓ X | ✓ X | ✓ X | ✓ X
Server Room 3 | ✓ X | ✓ X | ✓ X | ✓ X
Leak Detection
Server Rooms | ✓ X | ✓ X | ✓ X | ✓ X
PDU 13 | ✓ X | ✓ X | ✓ X | ✓ X
Notes:

## Page_02
Server Room 2
CRAC 29 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 21 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 32 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
Humidifier |  | %RH |  | %RH |  | %RH |  | %RH
PDU 21 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 20 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 06 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 14 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
FM 200 |  |  | ✓ X |  |  |  | ✓ X
CRAC 27 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 28 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
SR2 CHW Loop | PSI |  | PSI |  | PSI |  | PSI
CRAC 17 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 16 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 19 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 18 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
PDU 17 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 16 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CRAC 34 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
FM 200 |  |  | ✓ X |  |  |  | ✓ X
CRAC 15 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 25 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 20 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
PDU 19 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 18 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 07 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 15 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
Tear off Sticky Mat | Yes / No |  | Yes / No |  | Yes / No |  | Yes / No
MDF
Tear off Sticky Mat | Yes / No |  | Yes / No |  | Yes / No |  | Yes / No
PDU 12 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CRAC 08 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
Humidifier | ✓ X | %RH | ✓ X | %RH | ✓ X | %RH | ✓ X | %RH
FM 200 |  |  | ✓ X |  |  |  | ✓ X
PDU 05 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CRAC 09 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
East Battery Room
Rail 2 Batteries
CU2 Battery Circuit Breaker | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
Eagle Eye Computer Alarms | vDC |  | vDC |  | vDC |  | vDC
| Ω |  | Ω |  | Ω |  | Ω
| °F |  | °F |  | °F |  | °F
DC Ground Fault Module below 6MA (Pre-alarm = 10MA, Alarm = 20MA) | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
Spare Battery Charger | vDC |  | vDC |  | vDC |  | vDC
| amps |  | amps |  | amps |  | amps

## Page_03
Rail 3 Batteries
Room Temperature | °F |  | °F |  | °F |  | °F
CU3 Battery Breaker is Closed | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
Eagle Eye Computer Alarms | vDC |  | vDC |  | vDC |  | vDC
| Ω |  | Ω |  | Ω |  | Ω
| °F |  | °F |  | °F |  | °F
DC ╧ Fault Module below 6MA (Pre-alarm = 10MA, Alarm = 20MA) | Yes / No |  | Yes / No |  | Yes / No |  | Yes / No
East UPS Room
Battery Room Hydrogen Monitor % Levels | EF4% / EF5% |  | EF4% / EF5% |  | EF4% / EF5% |  | EF4% / EF5%
Rail 2
** Ensure key is in locked position before touching STS display screen!! **
STS-2A on preferred Source #1 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
STS-2B on preferred Source #1 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
STS-2C on preferred Source #1 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
STS-2D on preferred Source #1 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CRAC 37 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 36 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CU2-M1_UPS 2 | kW-Out |  | kW-Out |  | kW-Out |  | kW-Out
| kVA-Out |  | kVA-Out |  | kVA-Out |  | kVA-Out
| ✓ Any Active Events? X |  | ✓ Any Active Events? X |  | ✓ Any Active Events? X |  | ✓ Any Active Events? X
MBB Module Battery Breaker is Closed | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CI2
CI2-B08 Breaker SPD with 3 Green lights (Protected) | Yes / No |  | Yes / No |  | Yes / No |  | Yes / No
CI2-B11 CU2-M1 Input Breaker is Closed | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CI2-B06 Static Bypass Breaker is Closed | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
Eaton Xpert Meter Events light is OFF (User=X & PW=X) | Yes / No |  | Yes / No |  | Yes / No |  | Yes / No
CI2-B05 Maintenance Bypass Breaker is Closed | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CO2
Eaton Breaker Interface Module II Alarm light is OFF | Yes / No |  | Yes / No |  | Yes / No |  | Yes / No
CO2-B18 Spare is Open | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CO2-B11 STS-2A is Closed | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CO2-B12 STS-2B is Closed | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CO2-B17 Spare is Open | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CO2-B13 STS-1A is Closed | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CO2-B14 STS-3B is Closed | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CO2-B15 STS-2C is Closed | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CO2-B16 STS-2D is Closed | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
Eaton Xpert Meter Events light is OFF (User=X & PW=X) | Yes / No |  | Yes / No |  | Yes / No |  | Yes / No
CO2-B01 CC-CO Isolation switch is Closed | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CC3
CC3-B05 (MBB) Breaker is Open | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CC3-B01 (MIB) Breaker is Closed | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CC3-B99 (LBB) Breaker is Open | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X

## Page_04
** Ensure key is in locked position before touching STS display screen!! **
STS3A is on preferred source 1 | ✓ / X | ✓ / X | ✓ / X | ✓ / X
STS3B is on preferred source 1 | ✓ / X | ✓ / X | ✓ / X | ✓ / X
EF 4 | Hz | Hz | Hz | Hz
EF 5 | Hz | Hz | Hz | Hz
East Electrical Room Leak Detection | ✓ / X | ✓ / X | ✓ / X | ✓ / X
Tear off sticky mat for SR3 (East side) | Yes / No | Yes / No | Yes / No | Yes / No
Fire Pump/ Pre-Action Room
On 20:00 round only, check pre-action valves verifying open position, checkmark zone if True): | ✓ / X | ✓ / X | ✓ / X | ✓ / X
| ✓ / X | ✓ / X | ✓ / X | ✓ / X
| ✓ / X | ✓ / X | ✓ / X | ✓ / X
| ✓ / X | ✓ / X | ✓ / X | ✓ / X
| ✓ / X | ✓ / X | ✓ / X | ✓ / X
| ✓ / X | ✓ / X | ✓ / X | ✓ / X
Jockey pump controller in Auto | Yes / No | Yes / No | Yes / No | Yes / No
Fire pump controller in Auto | Yes / No | Yes / No | Yes / No | Yes / No
Fire pump is on Normal source power | Yes / No | Yes / No | Yes / No | Yes / No
System water pressure left side of controller (140 -150psi)
System Nitorgen PSI (inside the red cabinet)
Nitrogen Tank Regulator (Nitrogen_Extra-Dry_2000PSI)
Main building water meter (Total) readings (Top reading)
Is Building Main-Drain Water Leaking? | Yes / No | Yes / No | Yes / No | Yes / No
If drain pipe has water leaking, check the air-bleed-off-valve in the penthouse stairwell for leaks.
Loading Dock Area
Do we need to order salt? If yes let the Chief Engineer know. | Yes / No | Yes / No | Yes / No | Yes / No
Check brine level (should be at the indicating line). | ✓ / X | ✓ / X | ✓ / X | ✓ / X
HP LL- 5 Ok (Fan is ok, pipe sweating noticed, HP operation) | ✓ / X | ✓ / X | ✓ / X | ✓ / X
Mechanical / Chill Water Units Room
Cooling Twr. Supply water meter reading.
Water Softener (Qty: 3) Gallon Readings | Softener#1 | Softener#1 | Softener#1 | Softener#1
| Softener#2 | Softener#2 | Softener#2 | Softener#2
| Softener#3 | Softener#3 | Softener#3 | Softener#3
Well meter reading
HP LL- 4 Ok (Fan is ok, pipe sweating noticed, HP operation) | ✓ / X | ✓ / X | ✓ / X | ✓ / X
CHWP #3 | DP | DP | DP | DP
CHWP #5 | DP | DP | DP | DP
CHWP #2 | DP | DP | DP | DP
CHWP #4 | DP | DP | DP | DP
CHWP #1 | DP | DP | DP | DP
CDW to CHW makeup | DP | DP | DP | DP
CHW | DP | DP | DP | DP
CHW Filter PSI (23psi) | psi | psi | psi | psi
Bladder tank pressure (<30) | psi | psi | psi | psi
CHW Lakos Bag filter | DP | DP | DP | DP
Notes:

## Page_05
Condenser Supply_East (Normal = 68 to 85) | °F |  | °F |  | °F |  | °F
CWP-6 VFD | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz
CWP-1 VFD | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz
CWP-4 VFD | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz
CWP-3 VFD | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz
CDWF VFD | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz
CWP-2 VFD | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz
CWP-5 VFD | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz
TWR Fan- 6 VFD | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz
TWR Fan- 5 VFD | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz
CHWR Header Temp East | °F |  | °F |  | °F |  | °F
CHWR Temp (Bypass) East | °F |  | °F |  | °F |  | °F
Lakos Separator (6psi) | DP |  | DP |  | DP |  | DP
CHWS Temp East | °F |  | °F |  | °F |  | °F
CHWP #3 VFD | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz
Well VFD | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz
CHWP #2 VFD | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz
CHWP #4 VFD | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz
CHWP #1 VFD | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz
CHWP #5 VFD | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz
EF #6 VFD | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz
Core Pump #1 VFD | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz
Core Pump #2 VFD | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz
HP LL- 3 Ok (Fan is ok, pipe sweating noticed, HP operation) | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz
Core Pump #2 (15 - 20 PSID) | DP |  | DP |  | DP |  | DP
Core Pump #1 (15 - 20 PSID) | DP |  | DP |  | DP |  | DP
Condenser Supply_West (Normal = 68 to 85) | °F |  | °F |  | °F |  | °F
Chemical tanks level (above the order lines) | ✓ / X |  | ✓ / X |  | ✓ / X |  | ✓ / X
Nalco controller | ✓ / X |  | ✓ / X |  | ✓ / X |  | ✓ / X
Coupon Rack flow is between 4 – 6 GPM | GPM |  | GPM |  | GPM |  | GPM
Tower #4 VFD | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz
Tower #3 VFD | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz
Tower #2 VFD | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz
Tower #1 VFD | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz | ✓ / X | Hz
Core Filter PSI (38 to 45 psi) | PSI |  | PSI |  | PSI |  | PSI
HEX Core Water Temp In | °F |  | °F |  | °F |  | °F
HEX Core Water Temp Out | °F |  | °F |  | °F |  | °F
HEX Cond Water Temp In | °F |  | °F |  | °F |  | °F
HEX Cond Water Temp Out | °F |  | °F |  | °F |  | °F
HEX Cond DP (10psi min.) | PSI |  | PSI |  | PSI |  | PSI
HEX Core DP (150” PSID) | PSI |  | PSI |  | PSI |  | PSI
West sump level | inHg |  | inHg |  | inHg |  | inHg
TWP 5 DP | DP |  | DP |  | DP |  | DP
TWP 2 DP | DP |  | DP |  | DP |  | DP
TWP 3 DP | DP |  | DP |  | DP |  | DP
TWP 4 DP | DP |  | DP |  | DP |  | DP
Notes:

## Page_06
TWP 1 DP | DP | DP | DP | DP
TWP 6 DP | DP | DP | DP | DP
East Sump Level | inH2O | inH2O | inH2O | inH2O
Lakos cond. Water(7 PSID) | DP | DP | DP | DP
ATS-HPB-H Load on Normal | ✓ / X | ✓ / X | ✓ / X | ✓ / X
Chiller #1
In Recycle mode?? If so, fill out bold items | Yes / No | Yes / No | Yes / No | Yes / No
Is online?? If not, fill out only the last 3 bold items | Yes / No | Yes / No | Yes / No | Yes / No
Evap PSID 40” – 70” | DP | DP | DP | DP
Cond PSID 40” – 70” | DP | DP | DP | DP
CHW In temp. ≤ 65 deg. | °F | °F | °F | °F
CHW Out temp. 44 – 57deg. | °F | °F | °F | °F
Evap Ref. 43 – 56 deg. | °F | °F | °F | °F
CDW In Temp. 60- 90 deg. | °F | °F | °F | °F
CDW Out Temp. <CWP + 10 deg. | °F | °F | °F | °F
Cond. Ref. (65 – 115deg.) | °F | °F | °F | °F
Oil Pressure (25- 35 Psi) | PSI | PSI | PSI | PSI
Oil Temp. (70- 130 deg.) | °F | °F | °F | °F
Running in CCN mode | Yes / No | Yes / No | Yes / No | Yes / No
Manual/Auto switch in Auto | Yes / No | Yes / No | Yes / No | Yes / No
HP LL- 2 Ok (Fan is ok, pipe sweating noticed, HP operation) | ✓ / X | ✓ / X | ✓ / X | ✓ / X
Chiller #2
In Recycle mode?? If so, fill out bold items | Yes / No | Yes / No | Yes / No | Yes / No
Is online?? If not, fill out only the last 3 bold items | Yes / No | Yes / No | Yes / No | Yes / No
Evap PSID 40” – 70” | DP | DP | DP | DP
Cond PSID 40” – 70” | DP | DP | DP | DP
CHW In temp. ≤ 65 deg. | °F | °F | °F | °F
CHW Out temp. 44 – 57deg. | °F | °F | °F | °F
Evap Ref. 43 – 56 deg. | °F | °F | °F | °F
CDW In Temp. 60- 90 deg. | °F | °F | °F | °F
CDW Out Temp. <CWP + 10 deg. | °F | °F | °F | °F
Cond. Ref. (65 – 115deg.) | °F | °F | °F | °F
Oil Pressure (25- 35 Psi) | PSI | PSI | PSI | PSI
Oil Temp. (70- 130 deg.) | °F | °F | °F | °F
Running in CCN mode | Yes / No | Yes / No | Yes / No | Yes / No
Manual/Auto switch in Auto | Yes / No | Yes / No | Yes / No | Yes / No
Chiller #3
In Recycle mode?? If so, fill out bold items | Yes / No | Yes / No | Yes / No | Yes / No
Is online?? If not, fill out only the last 3 bold items | Yes / No | Yes / No | Yes / No | Yes / No
Evap PSID 40” – 70” | DP | DP | DP | DP
Cond PSID 40” – 70” | DP | DP | DP | DP
CHW In temp. ≤ 65 deg. | °F | °F | °F | °F
CHW Out temp. 44 – 57deg. | °F | °F | °F | °F
Evap Ref. 43 – 56 deg. | °F | °F | °F | °F
CDW In Temp. 60- 90 deg. | °F | °F | °F | °F
CDW Out Temp. <CWP + 10 deg. | °F | °F | °F | °F
Cond. Ref. (65 – 115deg.) | °F | °F | °F | °F
Oil Pressure (25- 35 Psi) | PSI | PSI | PSI | PSI
Oil Temp. (70- 130 deg.) | °F | °F | °F | °F
Running in CCN mode | Yes / No | Yes / No | Yes / No | Yes / No
Manual/Auto switch in Auto | Yes / No | Yes / No | Yes / No | Yes / No
Notes

## Page_07
Mechanical / Chill Water Units Room continued
Lakos filter (Big) PSI | In / Out | In / Out | In / Out | In / Out
Lakos filter (Small) PSI | ✓ / X | ✓ / X | ✓ / X | ✓ / X
Flow Max filter | PSI | PSI | PSI | PSI
West side CHW | DP | DP | DP | DP
Refrigerant Monitor | Alarms Yes / No | Alarms Yes / No | Alarms Yes / No | Alarms Yes / No
Refrigerant Monitor | Faults Yes / No | Faults Yes / No | Faults Yes / No | Faults Yes / No
HP LL- 1 Ok (Fan is ok, pipe sweating noticed, HP operation) | ✓ / X | ✓ / X | ✓ / X | ✓ / X
CHW Temp West | °F | °F | °F | °F
Rail 1 UPS Annunciator panel | ✓ / X | ✓ / X | ✓ / X | ✓ / X
Rail 2 UPS Annunciator panel | ✓ / X | ✓ / X | ✓ / X | ✓ / X
Rail 3 UPS Annunciator panel | ✓ / X | ✓ / X | ✓ / X | ✓ / X
DP 2 Breakers
DP2-B17 Spare Breaker is Open | ✓ / X | ✓ / X | ✓ / X | ✓ / X
DP2-B18 ATS-HPB1-C Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X
DP2-B19 ATS-HPA1-C Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X
DP2-B20 Spare Breaker is Open | ✓ / X | ✓ / X | ✓ / X | ✓ / X
DP2-B08 SPD All 3 Green lights (Protected) | Yes / No | Yes / No | Yes / No | Yes / No
DP2-B11 ATS-HPB-H Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X
DP2-B12 CHILLER 2 Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X
DP2-B13 ATS-HPB-C Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X
DP2-B14 SPARE Breaker is Open | ✓ / X | ✓ / X | ✓ / X | ✓ / X
DP2-B15 T-LBP-0 Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X
DP 1 Breakers | ✓ / X | ✓ / X | ✓ / X | ✓ / X
DP1-B21 Alt. Feed from MSB3 Breaker is Open
DP1-B16 T-PPLL01 Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X
DP1-B17 ATS-HPD-H Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X
DP1-B18 ATS-HPC1-C Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X
DP1-B19 ATS-HPA1-C Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X
DP1-B20 SPARE Breaker is Open | ✓ / X | ✓ / X | ✓ / X | ✓ / X
DP1-B08 SPD All 3 Green lights (Protected) | Yes / No | Yes / No | Yes / No | Yes / No
DP1-B11 ATS-HPB-H Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X
DP1-B12 CHILLER 1 Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X
DP1-B13 ATS-HPA-C Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X
DP1-B14 ATS-HPA-H Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X
DP1-B15 T-HLA-0 Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X
MSB 3
MSB3-B12 CI3 Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X
MSB3-B13 DP3 Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X
Eaton Xpert meter Events light OFF (User is X and PW is X) | Yes / No | Yes / No | Yes / No | Yes / No
MSB3-B01 Main Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X
MSB3-B08 SPD All 3 Green lights (Protected) | Yes / No | Yes / No | Yes / No | Yes / No
RPTCS (S1 lights are on) | Yes / No | Yes / No | Yes / No | Yes / No
Mode Switch is in the Closed Transition position | Yes / No | Yes / No | Yes / No | Yes / No
Notes

## Page_08
Mechanical / Chill Water Units Room continued
DP 3 Breakers
DP3-B08 SPD All 3 Green lights (Protected) | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No
DP3-B12 CHILLER 3 Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X
DP3-B13 ATS-HPC-C Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X
DP3-B14 ATS-HPC-H Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X
DP3-B15 MUA 4 Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X
DP3-B17 ATS-HPD-H Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X
DP3-B18 ATS-HPC1-C Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X
DP3-B19 ATS-HPB1-C Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X
DP3-B20 Spare Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X
MAU 3 VFD_Alarms | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No
Remote Radiator RR1 VFD in Auto | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No
Remote Radiator RR2 VFD in Auto | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No
Remote Radiator RR3 VFD in Auto | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No
ATS-HPD-H Load on Normal | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No
ATS-HPA1-C Load on Normal | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No
ATS-HPB1-C Load on Normal | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No
ATS-HPC1-C Load on Normal | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No
MSB 2
MSB2-B12 CI2 Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X
MSB2-B13 DP2 Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X
MSB2-B14 DP1 Temp Feed Breaker is racked out
Eaton Xpert meter Events light off | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No
MSB2-B01 Main Breaker is Closed | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X
MSB2-B08 SPD All 3 Green lights (Protected) | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No
RPTCS (S1 lights are on) | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No
Mode Switch is in the `Closed Transition position | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No
Tower Yard
Check the Towers for any Leaks and noises (Bearings, Belts ect.) | Running | Okay | Running | Okay | Running | Okay | Running | Okay
Tower 1 | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X
Tower 2 | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X
Tower 3 | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X
Tower 4 | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X
Tower 5 | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X
Tower 6 | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X
MUA 3 Status and Coils are clean and OK | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No
Fuel Storage Room 1
Total Gallons of Fuel | Gals | Gals | Gals | Gals | Gals | Gals | Gals | Gals
Leak detection panel | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X
Room Temperature | °F | °F | °F | °F | °F | °F | °F | °F
EF | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X | ✓ / X
1000 Gallon Day Tank Level | % | % | % | % | % | % | % | %
Alarms | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No | Yes / No
Notes

## Page_09
Fuel Storage Room 2
What fuel tank is selected | 1 or 2
Leak detection panel | ✓ / X | ✓ / X
Room Temperature | F
EF | ✓ / X | ✓ / X
Total Gallons of Fuel | Gals | Gals
Generator Room
Air Compressor oil level
Generator 3
PRV 6 VFD is in Auto | ✓ / X | Hz
FPCP Breaker is Closed | ✓ / X | ✓ / X
ATS-EB Breaker is Closed | ✓ / X | ✓ / X
LGS3-B03 ATS-MSB 3 Breaker is Closed | ✓ / X | ✓ / X
Generator 3 Coolant Temperature (˃100) | F
Day Tank Alarm_Gen3 | ✓ / X | ✓ / X
Day Tank Alarm_Gen2 | ✓ / X | ✓ / X
Battery Voltage | vDC
Battery Current | amps
Oil Temperature (If left, mark 105°F) | F
Generator 2
PRV 5 VFD is in Auto | ✓ / X | Hz
LGS2-B03 ATS-MSB 2 Breaker is Closed | ✓ / X | ✓ / X
Generator 2 Coolant Temperature (˃100) | F
Battery Voltage | vDC
Battery Current | amps
Oil Temperature (If left, mark 105°F) | F
Generator 1
PRV 4 VFD is in Auto | ✓ / X | Hz
LGS1-B03 ATS-MSB 1 Breaker is Closed | ✓ / X | ✓ / X
Generator 1 Coolant temp. (˃100) | F
Day tank Alarms | ✓ / X | ✓ / X
Battery Voltage | vDC
Battery Current | amps
Oil Temperature (If left, mark 105°F) | F
Oil Temperature (If left, mark 105°F) | F
PRV 7 VFD is in Auto | ✓ / X | Hz
Workshop
Fuel tank 1 Total Gallons | Gals | Gals
Fuel tank 2 Total Gallons | Gals | Gals
FCU- 9 VFD in Auto | ✓ / X | Hz
E-Service
Fire pump breaker is Closed | ✓ / X | ✓ / X
Room Temperature | F
Notes

## Page_11
Server Room 1
Tear off sticky mat (Battery Room) | Yes / No |  | Yes / No |  | Yes / No |  | Yes / No
CRAC 24 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 23 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
SR1 CHW Loop | D/P |  | D/P |  | D/P |  | D/P
CRAC 04 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
PDU 11 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 09 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 02 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 04 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CRAC 26 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 05 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 06 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
PDU 01 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 08 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CRAC 33 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 07 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
Humidifier | ✓ X | %RH | ✓ X | %RH | ✓ X | %RH | ✓ X | %RH
FM 200 (2 tanks)
Tear off sticky mat (Hallway) | Yes / No |  | Yes / No |  | Yes / No |  | Yes / No
Server Room 3
Tear of sticky mat (Hallway) | Yes / No |  | Yes / No |  | Yes / No |  | Yes / No
CRAC 10 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 22 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 31 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
PDU 23 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 22 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 03 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 10 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CRAC 11 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 12 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 13 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 14 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 30 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
Humidifier | ✓ X | %RH | ✓ X | %RH | ✓ X | %RH | ✓ X | %RH
FM 200
Tear off sticky mat (Loading Dock) | Yes / No |  | Yes / No |  | Yes / No |  | Yes / No
Final Notes: