## Page_01
Note: When doing rounds be aware for unusual smells, sounds, sights, or anything not normal.
Engineer Initials:
Time of Round: | 02:00 | 08:00 | 14:00 | 20:00
DCF Office
Logs
Check Daily logs on Microsoft SharePoint | ✓ X | ✓ X | ✓ X | ✓ X
Check office white board for plant information | ✓ X | ✓ X | ✓ X | ✓ X
BMS
OAT (Over-the-Air Temperature) | °F | °F | °F | °F
Wet Bulb | °F | °F | °F | °F
Any BMS alarms? Note in comments below. | Yes / No | Yes / No | Yes / No | Yes / No
Chill Water Unit No. 1 | kW | kW | kW | kW
Chill Water Unit No. 2 | kW | kW | kW | kW
Chill Water Unit No. 3 | kW | kW | kW | kW
Cooling Load_Mechanical Screen | tR | tR | tR | tR
Tower Load_Mechanical Screen | tR | tR | tR | tR
Total Power Usage_Electrical Screen | kW | kW | kW | kW
DCF Power Usage_Electrical Screen | kW | kW | kW | kW
PUE_Electrical Screen
Electrical Room_1st Floor
Fire Panel (Check for alarms on fire panel display)
Fire Alarm | ✓ X | ✓ X | ✓ X | ✓ X
Pre-alarm | ✓ X | ✓ X | ✓ X | ✓ X
Security | ✓ X | ✓ X | ✓ X | ✓ X
Supervisory | ✓ X | ✓ X | ✓ X | ✓ X
System Trouble | ✓ X | ✓ X | ✓ X | ✓ X
Other Event | ✓ X | ✓ X | ✓ X | ✓ X
Electrical Room_Lower Level
Room Temperature | ✓ X | ✓ X | ✓ X | ✓ X
EF 1 | Hz | Hz | Hz | Hz
EF 2 | Hz | Hz | Hz | Hz
Command Center
Fire Panel (Check for alarms on fire panel display)
Fire alarm | ✓ X | ✓ X | ✓ X | ✓ X
Pre-alarm | ✓ X | ✓ X | ✓ X | ✓ X
Security | ✓ X | ✓ X | ✓ X | ✓ X
Supervisory | ✓ X | ✓ X | ✓ X | ✓ X
System Trouble | ✓ X | ✓ X | ✓ X | ✓ X
Other Event | ✓ X | ✓ X | ✓ X | ✓ X
Vesda's
Server Room 1 | ✓ X | ✓ X | ✓ X | ✓ X
Server Room 2 | ✓ X | ✓ X | ✓ X | ✓ X
Server Room 3 | ✓ X | ✓ X | ✓ X | ✓ X
Leak Detection
Server Rooms | ✓ X | ✓ X | ✓ X | ✓ X
PDU 13 | ✓ X | ✓ X | ✓ X | ✓ X
Notes:

## Page_02
Server Room 2
CRAC 29 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 21 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 32 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
Humidifier |  | %RH |  | %RH |  | %RH |  | %RH
PDU 21 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 20 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 06 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 14 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
FM 200 |  |  | ✓ X |  |  |  | ✓ X
CRAC 27 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 28 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
SR2 CHW Loop | PSI |  | PSI |  | PSI |  | PSI
CRAC 17 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 16 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 19 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 18 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
PDU 17 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 16 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CRAC 34 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
FM 200 |  |  | ✓ X |  |  |  | ✓ X
CRAC 15 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 25 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 20 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
PDU 19 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 18 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 07 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 15 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
Tear off Sticky Mat | Yes / No |  | Yes / No |  | Yes / No |  | Yes / No
MDF
Tear off Sticky Mat | Yes / No |  | Yes / No |  | Yes / No |  | Yes / No
PDU 12 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CRAC 08 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
Humidifier | ✓ X | %RH | ✓ X | %RH | ✓ X | %RH | ✓ X | %RH
FM 200 |  |  | ✓ X |  |  |  | ✓ X
PDU 05 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CRAC 09 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
East Battery Room
Rail 2 Batteries
CU2 Battery Circuit Breaker | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
Eagle Eye Computer Alarms | vDC |  | vDC |  | vDC |  | vDC
| Ω |  | Ω |  | Ω |  | Ω
| °F |  | °F |  | °F |  | °F
DC Ground Fault Module below 6MA (Pre-alarm = 10MA, Alarm = 20MA) | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
Spare Battery Charger | vDC |  | vDC |  | vDC |  | vDC
| amps |  | amps |  | amps |  | amps

## Page_03
Rail 3 Batteries
Room Temperature | °F |  | °F |  | °F |  | °F
CU3 Battery Breaker is Closed | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
Eagle Eye Computer Alarms | vDC |  | vDC |  | vDC |  | vDC
| Ω |  | Ω |  | Ω |  | Ω
| °F |  | °F |  | °F |  | °F
DC ╧ Fault Module below 6MA (Pre-alarm = 10MA, Alarm = 20MA) | Yes / No |  | Yes / No |  | Yes / No |  | Yes / No
East UPS Room
Battery Room Hydrogen Monitor % Levels | EF4% / EF5% |  | EF4% / EF5% |  | EF4% / EF5% |  | EF4% / EF5%
Rail 2
** Ensure key is in locked position before touching STS display screen!! **
STS-2A on preferred Source #1 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
STS-2B on preferred Source #1 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
STS-2C on preferred Source #1 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
STS-2D on preferred Source #1 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CRAC 37 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 36 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CU2-M1_UPS 2 | kW-Out |  | kW-Out |  | kW-Out |  | kW-Out
| kVA-Out |  | kVA-Out |  | kVA-Out |  | kVA-Out
| ✓ Any Active Events? X |  | ✓ Any Active Events? X |  | ✓ Any Active Events? X |  | ✓ Any Active Events? X
MBB Module Battery Breaker is Closed | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CI2
CI2-B08 Breaker SPD with 3 Green lights (Protected) | Yes / No |  | Yes / No |  | Yes / No |  | Yes / No
CI2-B11 CU2-M1 Input Breaker is Closed | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CI2-B06 Static Bypass Breaker is Closed | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
Eaton Xpert Meter Events light is OFF (User=X & PW=X) | Yes / No |  | Yes / No |  | Yes / No |  | Yes / No
CI2-B05 Maintenance Bypass Breaker is Closed | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CO2
Eaton Breaker Interface Module II Alarm light is OFF | Yes / No |  | Yes / No |  | Yes / No |  | Yes / No
CO2-B18 Spare is Open | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CO2-B11 STS-2A is Closed | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CO2-B12 STS-2B is Closed | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CO2-B17 Spare is Open | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CO2-B13 STS-1A is Closed | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CO2-B14 STS-3B is Closed | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CO2-B15 STS-2C is Closed | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CO2-B16 STS-2D is Closed | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
Eaton Xpert Meter Events light is OFF (User=X & PW=X) | Yes / No |  | Yes / No |  | Yes / No |  | Yes / No
CO2-B01 CC-CO Isolation switch is Closed | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CC3
CC3-B05 (MBB) Breaker is Open | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CC3-B01 (MIB) Breaker is Closed | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CC3-B99 (LBB) Breaker is Open | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X

## Page_04
1 | ** Ensure key is in locked position before touching STS display screen!! **
2 | STS3A is on preferred source 1 | ✓ / X | ✓ / X | ✓ / X | ✓ / X
3 | STS3B is on preferred source 1 | ✓ / X | ✓ / X | ✓ / X | ✓ / X
4 | EF 4 | Hz | Hz | Hz | Hz
5 | EF 5 | Hz | Hz | Hz | Hz
6 | East Electrical Room Leak Detection | ✓ / X | ✓ / X | ✓ / X | ✓ / X
7 | Tear off sticky mat for SR3 (East side) | Yes / No | Yes / No | Yes / No | Yes / No
8 | Fire Pump/ Pre action Room
9 | On 20:00 round only, check pre-action valves verifying open position, checkmark zone if True): | Zone 1 | ✓ / X | Zone 5 | ✓ / X
10 |  | Zone 2 | ✓ / X | Zone 6 | ✓ / X
11 | Jockey pump controller in Auto | Zone 3 | ✓ / X | Zone 7 | ✓ / X
12 | Fire pump controller in Auto | Zone 4 | ✓ / X | c0c0c0
13 | Fire pump is on Normal source power | Wet system level 1-4 |  |  | ✓ / X
14 | System water pressure left side of controller (140 -150psi) | Wet system level 0 (Corridors) |  |  | ✓ / X
15 | System Nitorgen PSI (inside the red cabinet) | ✓ / X | ✓ / X | ✓ / X | ✓ / X
16 | Nitrogen Tank Regulator (Nitrogen_Extra-Dry_2000PSI) | ✓ / X | ✓ / X | ✓ / X | ✓ / X
17 | Main building water meter (Total) readings (Top reading) | ✓ / X | ✓ / X | ✓ / X | ✓ / X
18 | Is Building Main-Drain Water Leaking?
19 | If drain pipe has water leaking, check the air-bleed-off-valve in the penthouse stairwell for leaks.
20 | Loading Dock Area
21 | Do we need to order salt? If yes let the Chief Engineer know.
22 | Check brine level (should be at the indicating line). | ✓ / X | ✓ / X | ✓ / X | ✓ / X
23 | HP LL- 5 Ok (Fan is ok, If there's sweating of pipes check operation of HP)
24 | Mechanical / Chill Water Units Room
25 | Cooling Twr. Supply water meter reading.
26 | Write down the water softener gallon readings from each softener. | ✓ / X | ✓ / X | ✓ / X | ✓ / X
27 |  | ✓ / X | ✓ / X | ✓ / X | ✓ / X
28 |  | Softener#3 | Softener#3 | Softener#3 | Softener#3
29 | Well meter reading
30 | HP LL- 4 Ok (Fan is ok, If there's sweating of pipes check operation of HP)
31 | CHWP #3
32 | CHWP #5 | DP | DP | DP | DP
33 | CHWP #2 | DP | DP | DP | DP
34 | CHWP #4 | DP | DP | DP | DP
35 | CHWP #1 | DP | DP | DP | DP
36 | CDW to CHW makeup | DP | DP | DP | DP
37 | CHW | psi | psi | psi | psi
38 | CHW Filter PSI (23psi) | psi | psi | psi | psi
39 | Bladder tank pressure (<30) | psi | psi | psi | psi
40 | CHW Lakos Bag filter
41 | Notes:

## Page_11
Server Room 1
Tear off sticky mat (Battery Room) | Yes / No |  | Yes / No |  | Yes / No |  | Yes / No
CRAC 24 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 23 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
SR1 CHW Loop | D/P |  | D/P |  | D/P |  | D/P
CRAC 04 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
PDU 11 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 09 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 02 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 04 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CRAC 26 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 05 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 06 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
PDU 01 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 08 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CRAC 33 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 07 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
Humidifier | ✓ X | %RH | ✓ X | %RH | ✓ X | %RH | ✓ X | %RH
FM 200 (2 tanks)
Tear off sticky mat (Hallway) | Yes / No |  | Yes / No |  | Yes / No |  | Yes / No
Server Room 3
Tear of sticky mat (Hallway) | Yes / No |  | Yes / No |  | Yes / No |  | Yes / No
CRAC 10 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 22 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 31 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
PDU 23 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 22 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 03 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
PDU 10 | ✓ X |  | ✓ X |  | ✓ X |  | ✓ X
CRAC 11 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 12 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 13 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 14 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
CRAC 30 | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz | ✓ X | Hz
Humidifier | ✓ X | %RH | ✓ X | %RH | ✓ X | %RH | ✓ X | %RH
FM 200
Tear off sticky mat (Loading Dock) | Yes / No |  | Yes / No |  | Yes / No |  | Yes / No
Final Notes: